## Inputs
INPUT CHECK
Parameter | Classical Solver | Plexos | Match | Notes
SYSTEM SETUP
Data center bus number | 4 |  | — | CRITICAL: Phase 2 used bus 1 final analysis was bus 4 as well, Plexos used bus 4
Data center load (MW) | 200 |  | — | 200
Time horizon (hours) | 24 |  | — | 24
Slack bus number | None |  | — | Plexos uses bus 1
Line losses enabled? | No |  | —
GENERATORS (one row each)
Gen at bus 1: cost ($/MWh) | 20 |  | — | 20
Gen at bus 2: cost ($/MWh) | 20 |  | — | 20
Gen at bus 3: cost ($/MWh) | 40 |  | — | '20, this should be 40
Gen at bus 6: cost ($/MWh) | 40 |  | — | 40
Gen at bus 8: cost ($/MWh) | 40 |  | — | 40
Gen max capacities checked line by line? |  |  |  | Compare all 5 offline, then mark Verified
TRANSMISSION LIMITS
Transformer 4-9 limit (MW) | 40 |  | — | ~40, key bottleneck
Transformer 5-6 limit (MW) | 80 |  | — | ~80, key bottleneck
Transformer 4-7 limit (MW) | 80 |  | —
All 20 branch limits checked line by line? |  |  |  | Compare full table offline, then mark Verified
BATTERIES
Number of batteries | 4 |  | — | 4
Power per unit (MW) | 50 |  | — | 50
Energy per unit (MWh) | 200 |  | — | 200
Round-trip efficiency (%) | 90 |  | — | 90
Starting state of charge (%) | 90 |  | — | 90
One battery per node? | yes |  | —
SCENARIO ALIGNMENT
Contingency: which generator is tripped? | pending |  | — | Must be the SAME unit in both models
Weather: load scaling factor | pending |  | — | Same multiplier in both models
PLEXOS COST ADJUSTMENTS (Andrew only)
Discount rate stripped out? |  |  | —
Tax rate stripped out? |  |  | —
Battery capital cost excluded from total? |  |  | —

## Results
RESULTS — Do the methods agree on where the batteries go?
BASE CASE (all generators available)
Metric | Classical Solver | Quantum VQA | Plexos | No-Storage | Notes
Selected buses (e.g. 2, 4, 6, 7) | 2,4,6,7 |  |  | N/A
Total dispatch cost ($) | 199804 |  |  | 228429
Gap vs. classical optimum (%) | 0 |  |  | N/A | 0% = found the optimum
Runtime | ~2 min |  |  | 1 s
CONTINGENCY CASE (generator tripped — same unit both models)
Metric | Classical Solver | Quantum VQA | Plexos | No-Storage | Notes
Selected buses (e.g. 2, 4, 6, 7) |  |  |  | N/A
Total dispatch cost ($)
Gap vs. classical optimum (%) |  |  |  | N/A | 0% = found the optimum
Runtime

## Assumptions
MODELING ASSUMPTIONS
Assumption | What We Assumed
Test system | IEEE 14-bus.
Power flow | INPUT NEEDED
Generator costs | Linear cost functions. Cheap units at $20/MWh, expensive units at $40/MWh.
Line limits | Tightened from the unlimited case14 defaults to create meaningful congestion (transformers 4-9 and 5-6 are the key bottlenecks).
Data center load | 200 MW flat load added at a single bus. Training-cycle and cooling variability referenced as future work, not modeled.
Batteries | 4 units, 50 MW / 200 MWh each, 90% round-trip efficiency.
Time horizon | 24-hour dispatch (Phase 2) extended to one week for Phase 3. Load pattern repeats daily.
Contingency | INPUT NEEDED
Weather scenario | INPUT NEEDED
Ancillary services | Not modeled. The DC model has no frequency, so ancillary markets are referenced as future work only.
Slack bus | Plexos uses bus 1 as the defined slack bus.
Plexos cost basis | Discount rate, tax rate, and placeholder battery capital cost stripped from Plexos totals so dispatch costs are directly comparable. PLEASE VERIFY