## PLEXOS PTDFs (Output)
|  | Injection Point | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Path | Bus From | Bus To | 1 | 10 | 11 | 12 | 13 | 14 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 4_DataCenter
1 | 1 | 2 | 0 | -0.64801 | -0.63913 | -0.63166 | -0.63302 | -0.64366 | -0.83803 | -0.74654 | -0.66751 | -0.61056 | -0.62992 | -0.65729 | -0.65729 | -0.65192 | -0.66751
2 | 1 | 5 | 0 | -0.35199 | -0.36087 | -0.36834 | -0.36698 | -0.35634 | -0.16197 | -0.25346 | -0.33249 | -0.38944 | -0.37008 | -0.34271 | -0.34271 | -0.34808 | -0.33249
3 | 10 | 11 | 0 | 0.2846 | -0.46502 | -0.17569 | -0.15221 | 0.031622 | 0 | 0.010507 | 0.017219 | -0.010321 | -0.20573 | 0.12025 | 0.12025 | 0.17445 | 0.017219
4 | 10 | 9 | 0 | 0.7154 | 0.46502 | 0.17569 | 0.15221 | -0.031622 | 0 | -0.010507 | -0.017219 | 0.010321 | 0.20573 | -0.12025 | -0.12025 | -0.17445 | -0.017219
5 | 11 | 6 | 0 | 0.2846 | 0.53498 | -0.17569 | -0.15221 | 0.031622 | 0 | 0.010507 | 0.017219 | -0.010321 | -0.20573 | 0.12025 | 0.12025 | 0.17445 | 0.017219
6 | 12 | 13 | 0 | -0.015698 | 0 | 0.47994 | -0.16867 | -0.088165 | 0 | 0 | 0 | 0 | 0.030216 | -0.017661 | -0.017661 | -0.025622 | 0
7 | 12 | 6 | 0 | 0.015698 | 0 | 0.52006 | 0.16867 | 0.088165 | 0 | 0 | 0 | 0 | -0.030216 | 0.017661 | 0.017661 | 0.025622 | 0
8 | 13 | 14 | 0 | -0.070611 | 0.030847 | 0.19509 | 0.24132 | -0.39657 | 0 | 0 | -0.011376 | 0 | 0.13591 | -0.079441 | -0.079441 | -0.11525 | -0.011376
9 | 13 | 6 | 0 | 0.054913 | -0.023989 | 0.28485 | 0.59001 | 0.30841 | 0 | 0 | 0 | 0 | -0.1057 | 0.061779 | 0.061779 | 0.089625 | 0
10 | 14 | 9 | 0 | -0.070611 | 0.030847 | 0.19509 | 0.24132 | 0.60343 | 0 | 0 | -0.011376 | 0 | 0.13591 | -0.079441 | -0.079441 | -0.11525 | -0.011376
11 | 2 | 3 | 0 | -0.13484 | -0.1273 | -0.12097 | -0.12212 | -0.13114 | 0.027343 | -0.53203 | -0.15137 | -0.10307 | -0.11949 | -0.14271 | -0.14271 | -0.13815 | -0.15137
12 | 2 | 4 | 0 | -0.28219 | -0.26641 | -0.25316 | -0.25557 | -0.27446 | 0.057224 | -0.14343 | -0.31678 | -0.2157 | -0.25008 | -0.29866 | -0.29866 | -0.28913 | -0.31678
13 | 2 | 5 | 0 | -0.23099 | -0.24541 | -0.25753 | -0.25532 | -0.23806 | 0.077406 | -0.071076 | -0.19935 | -0.29178 | -0.26035 | -0.21592 | -0.21592 | -0.22464 | -0.19935
14 | 3 | 4 | 0 | -0.13484 | -0.1273 | -0.12097 | -0.12212 | -0.13114 | 0.027343 | 0.46797 | -0.15137 | -0.10307 | -0.11949 | -0.14271 | -0.14271 | -0.13815 | -0.15137
15 | 4 | 4_DataCenter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1
16 | 4 | 5 | 0 | 0.22776 | 0.10215 | 0 | 0.015841 | 0.16621 | 0.080021 | 0.30709 | 0.50325 | -0.30164 | -0.02793 | 0.35894 | 0.35894 | 0.28302 | 0.50325
17 | 4 | 7 | 0 | -0.4097 | -0.31508 | -0.23559 | -0.25006 | -0.36333 | 0 | 0.011087 | 0.018169 | -0.01089 | -0.21708 | -0.63421 | -0.63421 | -0.45134 | 0.018169
18 | 4 | 9 | 0 | -0.23508 | -0.18079 | -0.13518 | -0.14348 | -0.20848 | 0 | 0 | 0.010425 | 0 | -0.12456 | -0.16611 | -0.16611 | -0.25897 | 0.010425
19 | 5 | 6 | 0 | -0.35521 | -0.50414 | -0.62923 | -0.60646 | -0.42819 | 0 | -0.017449 | -0.028595 | 0.017139 | -0.65836 | -0.19969 | -0.19969 | -0.28969 | -0.028595
20 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0
21 | 7 | 9 | 0 | -0.4097 | -0.31508 | -0.23559 | -0.25006 | -0.36333 | 0 | 0.011087 | 0.018169 | -0.01089 | -0.21708 | 0.36579 | 0.36579 | -0.45134 | 0.018169

## Shadow Price vs Flow (Output)
Property | Band | Datetime | Units | 1_5 | 2_4 | Property | Datetime | Units | 1_5 | 2_4
Shadow Price | 1 | 2025-01-01 | $/MW | 0 | 0 | Flow | 2025-01-01 | MW | 110.69 | 99.17
Shadow Price | 1 | 2025-01-01 01:00 | $/MW | 0 | 0 | Flow | 2025-01-01 01:00 | MW | 90.38 | 103.13
Shadow Price | 1 | 2025-01-01 02:00 | $/MW | 0 | 0 | Flow | 2025-01-01 02:00 | MW | 108.55 | 95.1
Shadow Price | 1 | 2025-01-01 03:00 | $/MW | 0 | 0 | Flow | 2025-01-01 03:00 | MW | 107.84 | 93.75
Shadow Price | 1 | 2025-01-01 04:00 | $/MW | 0 | 0 | Flow | 2025-01-01 04:00 | MW | 107.84 | 93.75
Shadow Price | 1 | 2025-01-01 05:00 | $/MW | 0 | 0 | Flow | 2025-01-01 05:00 | MW | 109.98 | 97.81
Shadow Price | 1 | 2025-01-01 06:00 | $/MW | 0 | 0 | Flow | 2025-01-01 06:00 | MW | 114.26 | 105.94
Shadow Price | 1 | 2025-01-01 07:00 | $/MW | 0 | 0 | Flow | 2025-01-01 07:00 | MW | 118.54 | 114.08
Shadow Price | 1 | 2025-01-01 08:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 08:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 09:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 09:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 10:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 10:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 11:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 11:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 12:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 12:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 13:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 13:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 14:00 | $/MW | 0 | 0 | Flow | 2025-01-01 14:00 | MW | 117.69 | 120
Shadow Price | 1 | 2025-01-01 15:00 | $/MW | 0 | 0 | Flow | 2025-01-01 15:00 | MW | 115.41 | 120
Shadow Price | 1 | 2025-01-01 16:00 | $/MW | 0 | 0 | Flow | 2025-01-01 16:00 | MW | 119.96 | 116.79
Shadow Price | 1 | 2025-01-01 17:00 | $/MW | 0 | 0 | Flow | 2025-01-01 17:00 | MW | 115.41 | 120
Shadow Price | 1 | 2025-01-01 18:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 18:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 19:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 19:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 20:00 | $/MW | 16.83 | 47.65 | Flow | 2025-01-01 20:00 | MW | 120 | 120
Shadow Price | 1 | 2025-01-01 21:00 | $/MW | 0 | 0 | Flow | 2025-01-01 21:00 | MW | 119.96 | 116.79
Shadow Price | 1 | 2025-01-01 22:00 | $/MW | 0 | 0 | Flow | 2025-01-01 22:00 | MW | 115.68 | 108.65
Shadow Price | 1 | 2025-01-01 23:00 | $/MW | 0 | 0 | Flow | 2025-01-01 23:00 | MW | 112.83 | 103.23

## Load by Node (Output)
Parent Name | Collection | Property | Band | Datetime | Units | 1 | 10 | 11 | 12 | 13 | 14 | 2 | 3 | 4 | 4_DataCenter | 5 | 6 | 7 | 8 | 9
System | Node | Load | 1 | 2025-01-01 | MW | 0 | 5.76 | 2.24 | 3.9 | 8.64 | 9.54 | 13.89 | 60.29 | 30.59 | 200 | 4.86 | 7.17 | 0 | 0 | 18.88
System | Node | Load | 1 | 2025-01-01 01:00 | MW | 0 | 5.4 | 2.1 | 3.66 | 8.1 | 8.94 | 13.02 | 56.52 | 28.68 | 200 | 4.56 | 6.72 | 0 | 0 | 17.7
System | Node | Load | 1 | 2025-01-01 02:00 | MW | 0 | 5.22 | 2.03 | 3.54 | 7.83 | 8.64 | 12.59 | 54.64 | 27.72 | 200 | 4.41 | 6.5 | 0 | 0 | 17.11
System | Node | Load | 1 | 2025-01-01 03:00 | MW | 0 | 5.04 | 1.96 | 3.42 | 7.56 | 8.34 | 12.15 | 52.75 | 26.77 | 200 | 4.26 | 6.27 | 0 | 0 | 16.52
System | Node | Load | 1 | 2025-01-01 04:00 | MW | 0 | 5.04 | 1.96 | 3.42 | 7.56 | 8.34 | 12.15 | 52.75 | 26.77 | 200 | 4.26 | 6.27 | 0 | 0 | 16.52
System | Node | Load | 1 | 2025-01-01 05:00 | MW | 0 | 5.58 | 2.17 | 3.78 | 8.37 | 9.24 | 13.45 | 58.4 | 29.64 | 200 | 4.71 | 6.94 | 0 | 0 | 18.29
System | Node | Load | 1 | 2025-01-01 06:00 | MW | 0 | 6.66 | 2.59 | 4.51 | 9.99 | 11.03 | 16.06 | 69.71 | 35.37 | 200 | 5.62 | 8.29 | 0 | 0 | 21.83
System | Node | Load | 1 | 2025-01-01 07:00 | MW | 0 | 7.74 | 3.01 | 5.25 | 11.61 | 12.81 | 18.66 | 81.01 | 41.11 | 200 | 6.54 | 9.63 | 0 | 0 | 25.37
System | Node | Load | 1 | 2025-01-01 08:00 | MW | 0 | 8.55 | 3.32 | 5.79 | 12.82 | 14.15 | 20.61 | 89.49 | 45.41 | 200 | 7.22 | 10.64 | 0 | 0 | 28.02
System | Node | Load | 1 | 2025-01-01 09:00 | MW | 0 | 8.82 | 3.43 | 5.98 | 13.23 | 14.6 | 21.27 | 92.32 | 46.84 | 200 | 7.45 | 10.98 | 0 | 0 | 28.91
System | Node | Load | 1 | 2025-01-01 10:00 | MW | 0 | 8.91 | 3.47 | 6.04 | 13.37 | 14.75 | 21.48 | 93.26 | 47.32 | 200 | 7.52 | 11.09 | 0 | 0 | 29.21
System | Node | Load | 1 | 2025-01-01 11:00 | MW | 0 | 8.82 | 3.43 | 5.98 | 13.23 | 14.6 | 21.27 | 92.32 | 46.84 | 200 | 7.45 | 10.98 | 0 | 0 | 28.91
System | Node | Load | 1 | 2025-01-01 12:00 | MW | 0 | 8.55 | 3.32 | 5.79 | 12.82 | 14.15 | 20.61 | 89.49 | 45.41 | 200 | 7.22 | 10.64 | 0 | 0 | 28.02
System | Node | Load | 1 | 2025-01-01 13:00 | MW | 0 | 8.55 | 3.32 | 5.79 | 12.82 | 14.15 | 20.61 | 89.49 | 45.41 | 200 | 7.22 | 10.64 | 0 | 0 | 28.02
System | Node | Load | 1 | 2025-01-01 14:00 | MW | 0 | 8.37 | 3.26 | 5.67 | 12.56 | 13.86 | 20.18 | 87.61 | 44.45 | 200 | 7.07 | 10.42 | 0 | 0 | 27.44
System | Node | Load | 1 | 2025-01-01 15:00 | MW | 0 | 8.28 | 3.22 | 5.61 | 12.42 | 13.71 | 19.96 | 86.66 | 43.98 | 200 | 6.99 | 10.3 | 0 | 0 | 27.14
System | Node | Load | 1 | 2025-01-01 16:00 | MW | 0 | 8.1 | 3.15 | 5.49 | 12.15 | 13.41 | 19.53 | 84.78 | 43.02 | 200 | 6.84 | 10.08 | 0 | 0 | 26.55
System | Node | Load | 1 | 2025-01-01 17:00 | MW | 0 | 8.28 | 3.22 | 5.61 | 12.42 | 13.71 | 19.96 | 86.66 | 43.98 | 200 | 6.99 | 10.3 | 0 | 0 | 27.14
System | Node | Load | 1 | 2025-01-01 18:00 | MW | 0 | 8.64 | 3.36 | 5.86 | 12.96 | 14.3 | 20.83 | 90.43 | 45.89 | 200 | 7.3 | 10.75 | 0 | 0 | 28.32
System | Node | Load | 1 | 2025-01-01 19:00 | MW | 0 | 8.82 | 3.43 | 5.98 | 13.23 | 14.6 | 21.27 | 92.32 | 46.84 | 200 | 7.45 | 10.98 | 0 | 0 | 28.91
System | Node | Load | 1 | 2025-01-01 20:00 | MW | 0 | 8.91 | 3.47 | 6.04 | 13.37 | 14.75 | 21.48 | 93.26 | 47.32 | 200 | 7.52 | 11.09 | 0 | 0 | 29.21
System | Node | Load | 1 | 2025-01-01 21:00 | MW | 0 | 8.1 | 3.15 | 5.49 | 12.15 | 13.41 | 19.53 | 84.78 | 43.02 | 200 | 6.84 | 10.08 | 0 | 0 | 26.55
System | Node | Load | 1 | 2025-01-01 22:00 | MW | 0 | 7.02 | 2.73 | 4.76 | 10.53 | 11.62 | 16.93 | 73.48 | 37.28 | 200 | 5.93 | 8.74 | 0 | 0 | 23.01
System | Node | Load | 1 | 2025-01-01 23:00 | MW | 0 | 6.3 | 2.45 | 4.27 | 9.45 | 10.43 | 15.19 | 65.94 | 33.46 | 200 | 5.32 | 7.84 | 0 | 0 | 20.65

## Generation by Hour (Output)
Parent Name | Property | Band | Datetime | Units | Gen 1 | Gen 2 | Gen 3 | Gen 4 | Gen 5 | Parent Name | Property | Band | Datetime | Units | Gen 1 | Gen 2 | Gen 3 | Gen 4 | Gen 5
System | Generation | 1 | 2025-01-01 | MW | 332 | 33.76 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 01:00 | MW | 215.4 | 140 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 01:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 02:00 | MW | 332 | 18.22 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 02:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 03:00 | MW | 332 | 13.04 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 03:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 04:00 | MW | 332 | 13.04 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 04:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 05:00 | MW | 332 | 28.58 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 05:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 06:00 | MW | 332 | 59.66 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 06:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 07:00 | MW | 332 | 90.74 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 07:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 08:00 | MW | 323.33 | 120.84 | 0 | 0 | 1.88 | System | SRMC | 1 | 2025-01-01 08:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 09:00 | MW | 323.14 | 123.06 | 0 | 0 | 7.62 | System | SRMC | 1 | 2025-01-01 09:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 10:00 | MW | 323.07 | 123.8 | 0 | 0 | 9.54 | System | SRMC | 1 | 2025-01-01 10:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 11:00 | MW | 323.14 | 123.06 | 0 | 0 | 7.62 | System | SRMC | 1 | 2025-01-01 11:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 12:00 | MW | 323.33 | 120.84 | 0 | 0 | 1.88 | System | SRMC | 1 | 2025-01-01 12:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 13:00 | MW | 323.33 | 120.84 | 0 | 0 | 1.88 | System | SRMC | 1 | 2025-01-01 13:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 14:00 | MW | 311.35 | 129.52 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 14:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 15:00 | MW | 299.51 | 138.77 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 15:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 16:00 | MW | 332 | 101.1 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 16:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 17:00 | MW | 299.51 | 138.77 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 17:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 18:00 | MW | 323.27 | 121.58 | 0 | 0 | 3.8 | System | SRMC | 1 | 2025-01-01 18:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 19:00 | MW | 323.14 | 123.06 | 0 | 0 | 7.62 | System | SRMC | 1 | 2025-01-01 19:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 20:00 | MW | 323.07 | 123.8 | 0 | 0 | 9.54 | System | SRMC | 1 | 2025-01-01 20:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 21:00 | MW | 332 | 101.1 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 21:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 22:00 | MW | 332 | 70.02 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 22:00 | $/MWh | 20 | 20 | 40 | 40 | 40
System | Generation | 1 | 2025-01-01 23:00 | MW | 332 | 49.3 | 0 | 0 | 0 | System | SRMC | 1 | 2025-01-01 23:00 | $/MWh | 20 | 20 | 40 | 40 | 40

## Generator Information (Input)
System | Gen 1 | Units | 1 | -
System | Gen 1 | Max Capacity | 332 | MW
System | Gen 1 | Min Stable Level | 50 | MW
System | Gen 1 | Fuel Price | 1 | $/MMBtu
System | Gen 1 | Heat Rate | 20000 | Btu/kWh
System | Gen 2 | Units | 1 | -
System | Gen 2 | Max Capacity | 140 | MW
System | Gen 2 | Min Stable Level | 20 | MW
System | Gen 2 | Fuel Price | 1 | $/MMBtu
System | Gen 2 | Heat Rate | 20000 | Btu/kWh
System | Gen 3 | Units | 1 | -
System | Gen 3 | Max Capacity | 100 | MW
System | Gen 3 | Min Stable Level | 20 | MW
System | Gen 3 | Fuel Price | 1 | $/MMBtu
System | Gen 3 | Heat Rate | 40000 | Btu/kWh
System | Gen 4 | Units | 1 | -
System | Gen 4 | Max Capacity | 100 | MW
System | Gen 4 | Min Stable Level | 20 | MW
System | Gen 4 | Fuel Price | 1 | $/MMBtu
System | Gen 4 | Heat Rate | 40000 | Btu/kWh
System | Gen 5 | Units | 1 | -
System | Gen 5 | Max Capacity | 100 | MW
System | Gen 5 | Min Stable Level | 20 | MW
System | Gen 5 | Fuel Price | 1 | $/MMBtu
System | Gen 5 | Heat Rate | 40000 | Btu/kWh

## Node Information (Input)
| Property | Value | Units |  | Action | Expression |  | Property | Value | Units |  | Action | Expression
1 | Is Slack Bus | Yes | Yes/No | 1 | = |  | 1 | Is Slack Bus | Yes | Yes/No | 1 | =
1 | Voltage | 138 | kV | 1 | = |  | 1 | Voltage | 138 | kV | 1 | =
10 | Voltage | 138 | kV | 1 | = |  | 10 | Voltage | 138 | kV | 1 | =
10 | Load | 9 | MW | 1 | × | Load_Profile | 10 | Load | 12.6 | MW | 1 | × | Load_Profile
11 | Voltage | 138 | kV | 1 | = |  | 11 | Voltage | 138 | kV | 1 | =
11 | Load | 3.5 | MW | 1 | × | Load_Profile | 11 | Load | 4.9 | MW | 1 | × | Load_Profile
12 | Voltage | 138 | kV | 1 | = |  | 12 | Voltage | 138 | kV | 1 | =
12 | Load | 6.1 | MW | 1 | × | Load_Profile | 12 | Load | 8.54 | MW | 1 | × | Load_Profile
13 | Voltage | 138 | kV | 1 | = |  | 13 | Voltage | 138 | kV | 1 | =
13 | Load | 13.5 | MW | 1 | × | Load_Profile | 13 | Load | 18.9 | MW | 1 | × | Load_Profile
14 | Voltage | 138 | kV | 1 | = |  | 14 | Voltage | 138 | kV | 1 | =
14 | Load | 14.9 | MW | 1 | × | Load_Profile | 14 | Load | 20.86 | MW | 1 | × | Load_Profile
2 | Voltage | 138 | kV | 1 | = |  | 2 | Voltage | 138 | kV | 1 | =
2 | Load | 21.7 | MW | 1 | × | Load_Profile | 2 | Load | 30.38 | MW | 1 | × | Load_Profile
3 | Voltage | 138 | kV | 1 | = |  | 3 | Voltage | 138 | kV | 1 | =
3 | Load | 94.2 | MW | 1 | × | Load_Profile | 3 | Load | 131.88 | MW | 1 | × | Load_Profile
4 | Voltage | 138 | kV | 1 | = |  | 4 | Voltage | 138 | kV | 1 | =
4 | Load | 47.8 | MW | 1 | × | Load_Profile | 4 | Load | 66.92 | MW | 1 | × | Load_Profile
4_DataCenter | Voltage | 138 | kV | 1 | = |  | 4_DataCenter | Voltage | 138 | kV | 1 | =
4_DataCenter | Units | 1 | - | 1 | = |  | 4_DataCenter | Units | 1 | - | 1 | =
4_DataCenter | Load | 200 | MW | 1 | = |  | 4_DataCenter | Load | 200 | MW | 1 | =
5 | Voltage | 138 | kV | 1 | = |  | 5 | Voltage | 138 | kV | 1 | =
5 | Load | 7.6 | MW | 1 | × | Load_Profile | 5 | Load | 10.64 | MW | 1 | × | Load_Profile
6 | Voltage | 138 | kV | 1 | = |  | 6 | Voltage | 138 | kV | 1 | =
6 | Load | 11.2 | MW | 1 | × | Load_Profile | 6 | Load | 15.68 | MW | 1 | × | Load_Profile
7 | Voltage | 138 | kV | 1 | = |  | 7 | Voltage | 138 | kV | 1 | =
8 | Voltage | 138 | kV | 1 | = |  | 8 | Voltage | 138 | kV | 1 | =
9 | Voltage | 138 | kV | 1 | = |  | 9 | Voltage | 138 | kV | 1 | =
9 | Load | 29.5 | MW | 1 | × | Load_Profile | 9 | Load | 41.3 | MW | 1 | × | Load_Profile

## Hourly Load Multipliers (Input)
Year | Month | Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2012 | 1 | 1 | 0.32143 | 0.32143 | 0.32143 | 0.35714 | 0.39286 | 0.46429 | 0.57143 | 0.64286 | 0.71429 | 0.78571 | 0.85714 | 0.92857 | 0.96429 | 1 | 0.96429 | 0.92857 | 0.85714 | 0.78571 | 0.71429 | 0.64286 | 0.57143 | 0.5 | 0.42857 | 0.35714

## Baseline Multipliers (Input)
Year | Month | Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2012 | 1 | 1 | 0.45 | 0.45 | 0.45 | 0.5 | 0.55 | 0.65 | 0.8 | 0.9 | 1 | 1.1 | 1.2 | 1.3 | 1.35 | 1.4 | 1.35 | 1.3 | 1.2 | 1.1 | 1 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5
This is the original load profile used in the Baseline solver (use_cases/ieee14/ieee14.py DAILY_FACTORS) — deeper night valley, sharper midday peak than the AI-sourced profile in the tab to the left. Swap this in for an apples-to-apples PLEXOS vs Baseline comparison run.
[12 empty] | Max Load | 259
New Variable Load
Year | Month | Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2012 | 1 | 1 | 116.55 | 116.55 | 116.55 | 129.5 | 142.45 | 168.35 | 207.2 | 233.1 | 259 | 284.9 | 310.8 | 336.7 | 349.65 | 362.6 | 349.65 | 336.7 | 310.8 | 284.9 | 259 | 233.1 | 207.2 | 181.3 | 155.4 | 129.5
New Variable Load Multipliers
Year | Month | Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2012 | 1 | 1 | 0.32143 | 0.32143 | 0.32143 | 0.35714 | 0.39286 | 0.46429 | 0.57143 | 0.64286 | 0.71429 | 0.78571 | 0.85714 | 0.92857 | 0.96429 | 1 | 0.96429 | 0.92857 | 0.85714 | 0.78571 | 0.71429 | 0.64286 | 0.57143 | 0.5 | 0.42857 | 0.35714
New Total Load
Year | Month | Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2012 | 1 | 1 | 316.55 | 316.55 | 316.55 | 329.5 | 342.45 | 368.35 | 407.2 | 433.1 | 459 | 484.9 | 510.8 | 536.7 | 549.65 | 562.6 | 549.65 | 536.7 | 510.8 | 484.9 | 459 | 433.1 | 407.2 | 381.3 | 355.4 | 329.5

## Line Ratings (Input)
Line | Property | Value | Unit
1_2 | Max Flow | 400 | MW
1_2 | Resistance | 0.01938 | pu
1_2 | Reactance | 0.05917 | pu
1_5 | Max Flow | 120 | MW
1_5 | Resistance | 0.05403 | pu
1_5 | Reactance | 0.22304 | pu
10_11 | Max Flow | 80 | MW
10_11 | Resistance | 0.08205 | pu
10_11 | Reactance | 0.19207 | pu
12_13 | Max Flow | 80 | MW
12_13 | Resistance | 0.22092 | pu
12_13 | Reactance | 0.19988 | pu
13_14 | Max Flow | 60 | MW
13_14 | Resistance | 0.17093 | pu
13_14 | Reactance | 0.34802 | pu
2_3 | Max Flow | 120 | MW
2_3 | Resistance | 0.04699 | pu
2_3 | Reactance | 0.19797 | pu
2_4 | Max Flow | 120 | MW
2_4 | Resistance | 0.05811 | pu
2_4 | Reactance | 0.17632 | pu
2_5 | Max Flow | 120 | MW
2_5 | Resistance | 0.05695 | pu
2_5 | Reactance | 0.17388 | pu
3_4 | Max Flow | 120 | MW
3_4 | Resistance | 0.06701 | pu
3_4 | Reactance | 0.17103 | pu
4_5 | Max Flow | 9999 | MW
4_5 | Resistance | 0.01335 | pu
4_5 | Reactance | 0.04211 | pu
4_7 | Max Flow | 80 | MW
4_7 | Resistance | 1e-08 | pu
4_7 | Reactance | 0.20912 | pu
4_9 | Max Flow | 40 | MW
4_9 | Resistance | 1e-08 | pu
4_9 | Reactance | 0.55618 | pu
4_DataCenter | Max Flow | 9999 | MW
4_DataCenter | Resistance | 1e-08 | pu
4_DataCenter | Reactance | 1e-08 | pu
5_6 | Max Flow | 80 | MW
5_6 | Resistance | 1e-08 | pu
5_6 | Reactance | 0.25202 | pu
6_11 | Max Flow | 80 | MW
6_11 | Resistance | 0.09498 | pu
6_11 | Reactance | 0.1989 | pu
6_12 | Max Flow | 60 | MW
6_12 | Resistance | 0.12291 | pu
6_12 | Reactance | 0.25581 | pu
6_13 | Max Flow | 120 | MW
6_13 | Resistance | 0.06615 | pu
6_13 | Reactance | 0.13027 | pu
7_8 | Max Flow | 80 | MW
7_8 | Resistance | 1e-08 | pu
7_8 | Reactance | 0.17615 | pu
7_9 | Max Flow | 100 | MW
7_9 | Resistance | 1e-08 | pu
7_9 | Reactance | 0.11001 | pu
9_10 | Max Flow | 200 | MW
9_10 | Resistance | 0.03181 | pu
9_10 | Reactance | 0.0845 | pu
9_14 | Max Flow | 80 | MW
9_14 | Resistance | 0.12711 | pu
9_14 | Reactance | 0.27038 | pu